## SECTION 085113 - ALUMINUM WINDOWS (Architectural)

*TO FINISH YOUR SPECIFICATION: 1. Please read, react to, then delete comments in red or *stars*. 2. Please add or delete options in green or (parentheses). 3. Please replace preceding standards with options in blue [brackets] or delete options in blue [brackets]. 4. Finally, please revise paragraph numbers and/or letters, as necessary.*

*BEFORE USING YOUR FINISHED SPECIFICATION: Permit Peerless to review your edits to confirm your selected options do not restrict your desired operation or reduce the tested performance.*

PART 1 - GENERAL

1.01  SECTION INCLUDES

- Material: aluminum windows as on the drawings and specified in this section.

- Installation: labor, tools, and material needed to install aluminum windows.

- Glass and glazing.

(1.02  PRODUCTS SUPPLIED BUT NOT INSTALLED)

*Enter description, e.g., extra insulating glass to be supplied and stored for the future*

(1.03  PRODUCTS INSTALLED BUT NOT SUPPLIED)

*Enter description, e.g., custom security glazing supplied by others to be installed in the interior operable glazed panel in the new window*

1.04  RELATED SECTIONS - Section 079200 – Joint Sealants

1.05  REFERENCES

- AAMA - American Architectural Manufacturers Association - www.aamanet.org

- AAMA/WDMA/CSA 101/I.S.2/A440-08 “NAFS - North American Fenestration Standard/Specification for windows, doors, and skylights”

- AAMA 501.8-12 “Standard Test Method for Determination of Resistance to Human Impact of Window Systems Intended for Use in Psychiatric Applications”

- AAMA 502-12 "Voluntary Specification for Field Testing of Newly Installed Fenestration Products"

- AAMA 611-12 "Voluntary Specification for Anodized Architectural Aluminum"

- AAMA 701/702-11 "Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals”

- AAMA 904-09 “Voluntary Specification for Multi-bar Hinges in Window Applications”

- AAMA 2605-13 “Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels”

- AAMA CW-10-12 "Care and Handling of Architectural Aluminum from Shop to Site"

- ASTM - American Society for Testing and Materials – www.astm.org

- ASTM E283-12 "Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen"

- ASTM E330-14 "Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights, and Curtain Walls by Uniform Static Air Pressure Difference"

- ASTM E331-09 "Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference"

- ASTM E547-09 "Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Cyclic Static Air Pressure Differential"

- ASTM E2190-10 "Standard Specification for Insulating Glass Unit Performance and Evaluation"

- ASTM F588-07 “Standard Test Methods for Measuring the Forced Entry Resistance of Window Assemblies, Excluding Glazing Impact”

- IGCC – Insulating Glass Certification Council – www.igcc.org

- NFRC – National Fenestration Rating Council – www.nfrc.org

  - NFRC 100-2010 “Procedure for Determining Fenestration Product U Factors”

  - NFRC 102-2010 “Procedure for Measuring the Steady-State Thermal Transmittance of Fenestration Systems”

- SGCC – Safety Glazing Certification Council – www.sgcc.org

  - ANSI Z97.1-09 “American National Standard for Safety Glazing Materials used in Buildings – Safety Performance Specifications and Methods of Test”

  - 16 CFR 1201 “Consumer Product Safety Commission Safety Standard for Architectural Glazing Materials – codified at Title 16, Part 1201 of the Code of Federal Regulations 2011 Edition”

1.06  SYSTEM DESCRIPTION

- AAMA Designation: AW-PG70-FW.

- Windows: 4-1/4" frame depth; extruded aluminum with integral structural thermal break installed by the window manufacturer in the main frame members; equal-leg main frame; exterior and interior finishes applied by the window manufacturer; frames assembled by the window manufacturer.

- Thermal break: The thermal break separating the exterior and interior main frame aluminum extrusions shall be a mechanical crimp-in-place system utilizing multi-directional glass fiber reinforced polyamide nylon multiple-tubular struts with locking mechanical connections to the aluminum extrusions. The thermal break shall not be compromised by hardware or metal fasteners.

- Exterior configuration: fixed; exterior plane of the insulating glass in line with the window exterior plane.

- Interior configuration: interior operable glazed panel; interior plane of the single glazing material in line with the window interior plane.

- Exterior fixed glazing: exterior ExxonMobil Santoprene™ foam gasket; 1” [1-3/8"] insulating glass; two weep holes under each glass pocket for drainage; foam backer rod and silicone heel bead forming an internal seal; interior Santoprene™ bulb gasket threaded into aluminum glazing beads; glass description in paragraph 2.04; glazed by the window manufacturer.

- Interior operable glazed panel glazing: 1/2” clear polycarbonate glazing with Sabic Lexan Model #SL-4855 or Sheffield Makralon 15; PVC wrap around gasket; glazing material description in paragraph 2.05; glazed by the window manufacturer.

1.07 PERFORMANCE REQUIREMENTS

- Conformance to AW-PG70-FW specifications in AAMA/WDMA/CSA 101/I.S.2/A440-08 when tests are performed on the prescribed 60" x 99" minimum test size with the following test results:

- Air Infiltration: not to exceed AAMA 101 standard of maximum .1 cfm/square foot when tested per ASTM E283-12 at a static air pressure difference of 6.24 psf.

- Water Penetration: no uncontrolled water leakage when tested per ASTM E331-09 and ASTM E547-09 at a static air pressure difference of 15 psf.

- Uniform Deflection: no more than L/175 when tested per ASTM E330-14 at a static air pressure difference of 70 psf.

- Uniform Structural Load: no glass breakage or permanent damage to fasteners, and maximum .2% permanent deformation of the span of any frame member when tested per ASTM E330-14 at a static air pressure difference of 105 psf.

- Forced Entry Resistance: reasonable security against forced entry and the test window shall achieve a Grade 40 when tested per ASTM F588-07.

- Thermal NFRC Simulation: thermal computer simulation per NFRC 100-2010 on a 48” x 72” test size glazed with 1” insulating glass made with exterior 1/4” glass with a soft coat low E coating on surface #2, argon gas in the airspace made with a stainless steel spacer, and 1/4” clear glass. And interior 1/2” clear polycarbonate glazing with Sabic Lexan Model #SL-4855 or Sheffield Makralon 15 with the following test result: Standardized Thermal Transmittance to be maximum 0.236 BTU/HR/SQ.FT/°F.

- Simulated Interior Human Impact Test: Conformance to AAMA 501.8-12 when tests are performed on a 48” x 72” test size with a 250 minimum pound impactor resulting in a force of 2000 minimum foot-pounds with the following test results:

- Impact test load did not breech or penetrate through the inner-most glazing layer.

- There was no damage to locking devices.

- The hinges did not disengage.

1.08  SUBMITTALS

- Shop drawings: window location chart; typical window elevations; details of assemblies and glazing details for units glazed by the window manufacturer.

- Product data: test reports from an AAMA-accredited laboratory; manufacturer's specifications.

- Samples: each specified finish for aluminum; other samples as requested.

1.09  QUALITY ASSURANCE

- Submit for prebid approval ten days prior to bid opening valid test reports or waiver from an AAMA-accredited laboratory conforming to test results in Paragraph 1.07, and a sample window representing the bid window except for color.

- Acceptance will be by addendum only as no verbal approvals will be allowed.

- Submit bid on prequalified products in prebid written addendum. Bidder must identify manufacturer and model of product on which the bid is based.

- Furnish a valid AAMA “Authorization for Product Certification” or waiver indicating that the windows for the project conform to AAMA/WDMA/CSA 101/I.S.2/A440-08.

- Furnish visible, permanent IGCC certification labels indicating compliance with ASTM E 2190-10 on the insulating glass units.

- Furnish visible, permanent SGCC certification labels indicating conformance to ANSI Z97.1-09 and/or 16 CFR 1201 on tempered glass lites, if included on the project, and laminated glass lites, if included on the project.

- Manufacturer's warranties:

- Windows: warrant for one year against defects in material or workmanship under normal use.

- Insulating glass units: warrant seal for ten years against visual obstruction from film formation or moisture collection between internal glass surfaces, excluding that caused by glass breakage or abuse.

- Paint finish: Finish conforming to AAMA 2605-13: warrant for twenty years against chipping, peeling, blistering, cracking, chalking, or fading.

(H. Project Survey: *Contact Peerless to register before project bid date* by installer

and manufacturer’s representatives; one year after date of completion; to

recommend maintenance procedures.)

  - DELIVERY, STORAGE, AND HANDLING - Handle and protect windows and

accessories in accordance with AAMA CW-10-12 until installation completion.

# PART 2 - PRODUCTS

2.01  MANUFACTURERS

- Peerless P541 Architectural Thermal Aluminum Psychiatric Window

- Other acceptable manufacturers who have demonstrated a successful history of manufacturing for *Enter number* years equivalent products:

- *Enter an equivalent manufacturer’s company name and model number*

- *Enter another equivalent manufacturer’s company name and model number*

2.02  MATERIALS

- Aluminum extrusions: extruded by the window manufacturer from commercial quality 6063-T5 alloy; free from defects impairing strength and durability.

- Weatherstrip: secured in extruded ports; Santoprene™ bulb seal conforming to AAMA 702-11 in internal aluminum glazing beads; PVC bulb seal conforming to AAMA 702-11 in double rows around the perimeter of the interior operable glazed panel.

- Interior Operable Glazed Panel Hardware: mounted in concealed extruded grooves to avoid penetrating frame or panel members with fasteners; two concealed stainless steel hinges conforming to AAMA 904-09 per panel to rotate the panel inward on vertical axis; one exposed single-action natural finish lock with multiple concealed locking points per panel; one 1/4” hex locking key for custodial access to the internal cavity between the fixed insulating glass and interior operable glazed panel.

2.03 FABRICATION

- Master Frame: double tubular head, sill, and jambs mitre cut and fastened with two zamac corner gussets per corner; corners sealed by window manufacturer with polyethylene foam gaskets.

- Interior Operable Glazed Panel: double tubular stiles and rails fastened with two zamac gussets per corner; joints sealed by window manufacturer with polyethylene foam gaskets.

- Water control: two frame sill exterior weep slots covered with weep flaps and weep hoods finished to match window.

2.04  EXTERIOR INSULATING GLASS UNITS

### Materials

- Spacer: tubular stainless steel.

- Spacer color: stainless metal color.

- Primary seal: polyisobutylene.

- Secondary seal: silicone.

- Airspace fill: plain air. [argon.]

### Performance

1.	Dual-seal durability: conformance to ASTM E 2190-10; visible, permanent IGCC certification label.

(2. Other: *Enter center-of-glass U value, SHGC, and VT data as required*)

- Exterior glass lite

- Thickness: 1/8". [3/16".] [1/4".]

- Tint: clear. [bronze.] [gray.] [green.]

- Type: annealed. [tempered.] [laminated. *Enter interlayer and lite descriptions*]

(4.  Coating: low E coating on #2 surface; Cardinal Glass 270 or Cardinal Glass

366 or equivalent.)

- Interior glass lite

- Thickness: 1/8". [3/16".] [1/4".]

- Tint: clear. [obscure. *Enter pattern*]

- Type: annealed. [tempered.] [laminated. *Enter interlayer and lite descriptions*]

(4.  Coating: low E coating on #3 surface; Cardinal Glass 270 or Cardinal Glass

366 or equivalent.)

(5.  Coating: low E coating on #4 surface; Cardinal Glass i89 or equivalent.)

- Glass surface protection: Factory-apply removeable protective clear Cardinal Glass Preserve™ film on insulating glass exterior and interior surfaces for protection during window installation and building construction.

2.05  INTERIOR GLAZING MATERIAL: 1/2” clear polycarbonate glazing with Sabic Lexan Model #SL-4855 or Sheffield Makralon 15.

2.06  FINISH ON EXTERIOR ALUMINUM EXTRUSIONS

    - Application: on clean extrusions free from objectionable surface blemishes; on exposed surfaces visible when installed product's operating sash is closed. Electrostatic spray by an Approved Applicator and appropriate oven bake process.

    - Coating: Superior Performance Powder coating: One-coat dry system with resin containing 70% fluoropolymer; thermosetting; alternative finishes will not be acceptable.

    - Quality Standard: Conforming to AAMA 2605-13, including 10 years Florida exposure. [AAMA 2604-13, including 5 years Florida exposure.]

    - Pretreatment: Mechanically clean and chemically pretreat fabricated items in accordance with coating manufacturer's requirements and AAMA requirements with a Chrome Free Treatment.

    - Coating Quantity: One single color coating, additional coating quantities will not be accepted. This includes, but is not limited to barrier coats, primers and clear coats.

    - Dry Film Thickness: Eighty percent of measurements on primary exposed surfaces shall exceed 1.9 mils with a standard thickness range of 1.9 to 3.14 mils, except inside corners and channels.

    - Environmental Factors: Less than 3% harmful VOC's (Volatile Organic Compounds) emitted during powder coating application process.

    - Color: Chosen from manufacturer's standards.

** NOTE TO SPECIFIER ** Delete exterior finish not required.

      - Quality Standard: Conforming to AAMA 2604.

      - Quality Standard: Conforming to AAMA 2605.

  - FINISH ON INTERIOR ALUMINUM EXTRUSIONS

    - Application: on clean extrusions free from objectionable surface blemishes; on exposed surfaces visible when installed product's operating sash is closed. Electrostatic spray by an Approved Applicator and appropriate oven bake process.

    - Coating: Superior Performance Powder coating: One-coat dry system with resin containing 70% fluoropolymer; thermosetting; alternative finishes will not be acceptable.

    - Quality Standard: Conforming to AAMA 2605-13, including 10 years Florida exposure. [AAMA 2604-13, including 5 years Florida exposure.]

    - Pretreatment: Mechanically clean and chemically pretreat fabricated items in accordance with coating manufacturer's requirements and AAMA requirements with a Chrome Free Treatment.

    - Coating Quantity: One single color coating, additional coating quantities will not be accepted. This includes, but is not limited to barrier coats, primers and clear coats.

    - Dry Film Thickness: Eighty percent of measurements on primary exposed surfaces shall exceed 1.9 mils with a standard thickness range of 1.9 to 3.14 mils, except inside corners and channels.

    - Environmental Factors: Less than 3% harmful VOC's (Volatile Organic Compounds) emitted during powder coating application process.

    - Color: Chosen from manufacturer's standards.

** NOTE TO SPECIFIER ** Delete interior finish not required.

      - Quality Standard: Conforming to AAMA 2604.

      - Quality Standard: Conforming to AAMA 2605.

(2.08  MUNTINS)

- Material: extruded aluminum; with exposed surfaces finished to match window color; concealed fasteners; designed for unrestricted expansion and contraction.

- Design: muntin bar cross-section profile and material chosen from manufacturer’s standards.

- Patterns: grid patterns to be designated by architect.

- Location: exterior. (internal: encapsulated between the two glass lites in the insulating glass unit to protect them from damage and dirt buildup.) [true: dividing the insulating glass into small individual units.]

(2.09  INSTALLATION ACCESSORIES)

- Material: extruded aluminum; nominal .062” wall; with exposed surfaces finished to match window color and finish performance; concealed fasteners; required weatherseals; designed for unrestricted expansion and contraction.

- Exterior: (snap-in sill panning leg.) (wrap around panning.) (preset panning.) (snap-in nailing fin.) (snap-in flange.) (two-piece receptor with polyamide strip thermal break.) (10 psf subsill with polyamide strip thermal break and end dams sealed by the window manufacturer.)

- Interior: (two-piece snap trim and trim clip.)

- Other: (steel strap anchor.) (head expander with polyamide strip thermal break.) (sill angle.)

PART 3 - EXECUTION

3.01  PREPARATION - Prepare openings to be in tolerance, plumb, level,  provide for

secure anchoring, and in accordance with approved shop drawings.

3.02  INSTALLATION

- Install windows in accordance with approved shop drawings and window manufacturer's recommendations with skilled craftspeople who have demonstrated a successful history of installing windows for *Enter number* years.

- Provide required support and securely fasten and set windows plumb, square, and level without twist or bow.

- Apply sealant per sealant manufacturer's recommendations at joints, wipe off excess, and leave exposed sealant surfaces clean and smooth.

(3.03  FIELD TESTING)

- Test installed units in conformance with AAMA 502-12 minimum requirements for air and water infiltration with the window manufacturer, dealer, contractor, and owner present.

- Select test units as directed by the owner's representative and use an AAMA-accredited laboratory provided by the owner or contractor not to be tested higher than 8psf or 2/3rd reduction of 12 psf.

3.04  ADJUSTING - Adjust windows as necessary for smooth and weathertight

operation.

3.05  CLEANING

- Peel the Preserve™ protective film from the window glass surfaces when the window installation is complete, leaving these surfaces ready for use without the need for glass cleaning.

- Leave the installed windows clean and free of construction debris.

3.06  CARE PRIOR TO BUILDING COMPLETION - Protect surfaces of installed

windows, in accordance with AAMA CW-10-12, from contact with

contaminating substances resulting from surrounding construction.

END OF SECTION